Test Procedure – Line to Battery Backup & Battery to Line Transition

- Conduct a visual inspection of the EUTs. Document and record any anomalies.

- Conduct an operational check of the EUTs

  - Verify all output voltages Correct

  - Verify power consumption per node

- Connect external backup batteries to AC source

- Turn the battery switch on the AC supply to the “ON” position

- Connect current clamp to the “Line” output of the AC source

  - Set Current clamp to 100 mv/A

  - Connect Current clamp output to CH3 of Oscilloscope

  - Set Oscilloscope attenuation to 10x

  - Set units to Current [A]

- Connect AC [CH1] / DC [CH2] output to Oscilloscope

  - DC - Set Oscilloscope probe attenuation to 10x

  - Set Channel V/div to 5v/Div (User discretion as needed)

  - AC – Set Oscilloscope probe to 50x

  - Set Channel to 100V/Div (User discretion as needed – Probe dependent)

- Set Oscilloscope acquisition to “Scroll” Mode and horizontal scale to 500mS/div

- Turn Power on AC source

- Turn each node on 1 though 7

- When all nodes are powered up (Green: DC Out, Green: AC IN) Switch the AC power off and capture the waveform when at the moment the AC power is removed. The XM supply will transition to battery back-up.

  - Note if any of the Nodes Green: DC OUT or Green: AN IN LEDs turn RED

    - Document any failures

  - Record the wave forms

- Wait 5 seconds

- Turn AC source back on

  - With the Oscilloscope in roll mode capture the event when the XM transitions from battery back-up to Line power

  - Note if any of the Nodes Green: DC OUT or Green: AN IN LEDs turn RED

    - Document any failures

  - Record the wave forms

- Wait 5 seconds

- Repeat steps 10 through 13 for TEN iterations. Observer and document any failures.

- Shut off one node

- Repeat steps 10 through 15 until one node is left. This will test a network configuration from all 7 nodes down to 1 node.

- Run test on all AC power sources (XM2, XM3)

Notes

- Test with dual and single supply configurations. Observe if they perform similarly.

- Do not forget to test with all configurations from 7 nodes to 1 node, with 7 nodes being the worst-case network topology.

- If nodes are not available, use a module-level network instead.

Power supply pictures: